Ke - Ke times ( {CV - CVe0} over {CVe - CVe0} ) ^ CVexp = Ke times ( 1 - ({Cv - CVe0} over {CVe - CVe0}) ^ CVexp), color blue {CV > CVe0} Ke, color blue {CV leslant CVe0} {dTt over dt} Tt sub { t + %DELTA t } = Tt sub t + dTt over dt times %DELTA t
Tank Bulk Temperature (dTt/dt) Model
Heat In: Ke
Ke represents exothermic heat (Ke > 0)
Temperature as proxy for (specific) heat
Units of deg/h
0.138-0.175ºC/h estimate based on slope of temperature rise on trend plot when CV=0 (no cooling); temperature as proxy for
Heat Out: f(CV)
Chilled glycol jacket
Three-parameter model:
CVe – CV at which f(CV) = Ke i.e. heat balance with exotherm
CVe0 – CV below which f(CV) = 0
CVexp – exponent of linear relation (CV-CVe0)/(CVe-CVe0)
Final result: In – Out = Ke - f(CV)
Implemented as: i.e. Explicit Euler integration
Caveats
Excludes heat loss to environment (Province of Alberta, CA - brrrrr)
Temperature is linear proxy for heat i.e. Ke units are ºC/h, not W
Ignore any dependence of [Heat In] (Ke) and [Heat Out] on Tt
=
{
dPV over dt = { Tt - PV } over %tau kPV = e ^{ -1 over %tau } PV sub { t + %DELTA t } = Tt sub t + ( PV sub t - Tt ) times kPV ^ { %DELTA t } + K sub e
Temperature sensor (dPV/dt) model
Heat in: Ke
Same as Tt above
Heat out: f(PV,Tt)
Fluid around sensor at PV in thermowell is thermally isolated from cooling jacket, but will be cooled by bulk tank media at Tt
PV will always be greater than, and decay towards, Tt
First-order diff. equation:
One-parameter model:
kPV is reduction of PV as it decays toward Tt in 1s
Implemented (nearly) as: